## Project
ENERGY CONCEPTS COMPANY |  |  |  |  | 2020-07-16
(410) 266-6521 | [8 empty] | Summary- This tool helps estimate Ammonia Absorption Refrigeration Unit (AARU) performance from basic data of interfacing utilities.
Basic layout of the system is shown in the figure.
User Input Parameters Are Highlighted in Red
[9 empty] | TChWS | Chill Water Supply Temperature | 45 | F | Based on process chilling requirements
Hint-higher the better
[9 empty] | TCWS | Cooling Water Supply Temperature | 60 | F | Based on site wet bulb temperature
Hint-lower the better
[10 empty] | Minimum Hot Water Return Temperature | 182.075 | F
[9 empty] | THWS | Hot Water Supply Temperature | 250 | F | Atleast 15-20F hotter than minimum hot water return temperature
Else increase TChWS or decrease TCWS
[9 empty] | GPMHW | Hot Water Flowrate | 40 | gpm
[6 empty] | 134.4948 | F
[6 empty] | 23.1 | gpm
| 45 | F | [7 empty] | Capacity Factor | 1.0629 |  | Close to or greater than 0.8 indicates potentially good application
|  |  |  | 60 | F | [7 empty] | Else increase TChWS, THWS and/or decrease TCWS
Other factors such as annual utilization and utility rates will impact economics
[6 empty] | 250 | F |  | QChW | AARU Maximum Chilling Capacity | 318.5874 | MBTUH
56.6722 | F | [9 empty] | 26.549 | RT
54.5 | gpm
[9 empty] | QHW | AARU Heat Input-Hot Water | 531.5839 | MBTUH
[7 empty] | 222.1773 | F
[7 empty] | 40 | gpm | COP | AARU Efficiency | 0.59932
[7 empty] | 531.5839 | MBTUH
[9 empty] | THWR | Hot Water Return Temperature | 222.1773 | F
[9 empty] | TChWR | Chill Water Return Temperature | 56.6722 | F | Suggested values-variations possible
[9 empty] | GPMChW | Chill Water Flowrate | 54.5 | gpm | Suggested values-variations possible
[9 empty] | TCWR | Cooling Water Return Temperature | 134.4948 | F | Suggested values-variations possible
|  |  | Capacity | 318.5874 | MBTUH
|  |  |  | 26.549 | RT |  |  |  | GPMCW | Cooling Water Flowrate | 23.1 | gpm | Suggested values-variations possible
[9 empty] | QCW | AARU Heat Rejection -Cooling Water | 850.1713 | MBTUH
Chill water return
Chill water supply
Process water supply
Process water Return
Hot water supply
Hot water return
AARU
EVAP
COND / ABS
GEN

## Characterization (hidden)
|  | cg1 | cg2 | cg3 | cg4 | ce0 | ce1 | ce2 | ce3 | ce4
|  | 2.5742 | 0.96888 | 0.91416 | 28.6011 | 0 | 3.6604 | 2.3027 | 0.37904 | 42.5872
[17 empty] | thwin | 250
[14 empty] | flows |  |  | thwo1
| 250 | 60 | 45 | [10 empty] | cooling | Chill | Hot | thwo2 | 105.654
[12 empty] | cop | rt | gpm | gpm | gpm | tcwin | 60
| tg | tac | te_out | dttg | qgen2 | tg | tac | te | dtte | qevap2 | [6 empty] | tcwo | 56.9416
| C | C | C | C | kW | C | C | C | C | kW | [6 empty] | tchwin | 13.7068
[17 empty] | tchwo | 45
| 250 | 60 | 45 | 139.1503 | 155.8073 | 250 | 60 | 45 | 133.9972 | 93.378 |  | 0.59932 | 26.5731 | 23.1 | 54.5 | 40 | tgo_min | 83.375
[17 empty] | Fcap | 1.0629
| tgo | tcwo | tei |  | Qg_Mbtuh |  |  |  |  | Qe_Mbtuh | [6 empty] | fqe | 0.99909
[14 empty] | Prorate |  |  | fqg
C | 105.654 | 56.9416 | 13.7068 |  | 531.5839 |  |  |  |  | 318.5874 | [6 empty] | fvh
F | 222.1773 | 134.4948 | 56.6722 | [13 empty] | fmin | 0.99909
[5 empty] | 531.5839 |  |  |  |  | 318.5874 |  |  | 26.549 | 23.1 | 54.5 | 40
qg1
| tgo_min | [15 empty] | qe2 | 93.293
[17 empty] | qg2 | 155.6655
C | 83.375 | [15 empty] | qcw | 248.9585
F | 182.075 | [15 empty] | COP | 0.59932
tgo
182.075
[17 empty] | vh | 7.4332
| 222.1773 |  |  |  | 531.5839 |  |  |  |  | 318.5874 | correct for tgo_min |  | 26.549 | 23.1 | 54.5 |  | vchw | 20.1816
[17 empty] | vcw | 35.9672